## Kaiser Permanente - San Lea-1
Customer: | Kaiser Permanente
Size (kW): | 2000
Name: | Kaiser Permanente - San Leandro
Location: | 2500 Merced St, San Leandro, CA
Kaiser Permanente - San Leandro
Date (Local) | Total Output Factor | AC Efficiency (LHV) | Heat Rate (HHV) | Electricity Out
| % | % | BTU/kWh | kWh
Custom | 71.68% | 51.51% | 7336.2116 | 12583576
Date (Local) | Total Output Factor | AC Efficiency (LHV) | Heat Rate (HHV) | Electricity Out
| % | % | BTU/kWh | kWh
2022-06-01 | 72.21% | 51.07% | 7400.2294 | 34660
2022-06-02 | 72.13% | 51.04% | 7404.8338 | 34624
2022-06-03 | 72.09% | 51.03% | 7405.2293 | 34604
2022-06-04 | 72.1% | 51.05% | 7403.3975 | 34608
2022-06-05 | 70.05% | 50.74% | 7447.5233 | 33624
2022-06-06 | 69.73% | 50.67% | 7457.7453 | 33468
2022-06-07 | 71.93% | 51.04% | 7404.7981 | 34528
2022-06-08 | 71.92% | 51.05% | 7402.7546 | 34524
2022-06-09 | 71.87% | 51.02% | 7407.4307 | 34496
2022-06-10 | 71.69% | 50.98% | 7413.5526 | 34412
2022-06-11 | 71.17% | 50.96% | 7416.3371 | 34160
2022-06-12 | 71.54% | 50.98% | 7412.9544 | 34340
2022-06-13 | 71.57% | 50.99% | 7410.9722 | 34352
2022-06-14 | 71.48% | 50.96% | 7415.2744 | 34312
2022-06-15 | 71.39% | 50.95% | 7417.5588 | 34268
2022-06-16 | 71.38% | 50.94% | 7418.8505 | 34260
2022-06-17 | 71.43% | 50.92% | 7421.0004 | 34288
2022-06-18 | 71.28% | 50.89% | 7426.2155 | 34216
2022-06-19 | 71.13% | 50.89% | 7426.173 | 34144
2022-06-20 | 70.99% | 50.83% | 7435.4426 | 34076
2022-06-21 | 70.93% | 50.8% | 7439.4395 | 34044
2022-06-22 | 70.49% | 50.81% | 7437.5748 | 33836
2022-06-23 | 70.13% | 50.89% | 7425.7541 | 33664
2022-06-24 | 70.04% | 50.88% | 7427.2507 | 33620
2022-06-25 | 70.03% | 50.89% | 7425.8902 | 33616
2022-06-26 | 70.01% | 50.91% | 7423.4325 | 33604
2022-06-27 | 70% | 50.91% | 7423.168 | 33600
2022-06-28 | 69.96% | 50.89% | 7426.2433 | 33580
2022-06-29 | 69.77% | 50.85% | 7431.7879 | 33488
2022-06-30 | 68.23% | 50.72% | 7450.2019 | 32752
2022-07-01 | 68.97% | 50.7% | 7454.3304 | 33104
2022-07-02 | 68.89% | 50.68% | 7456.6692 | 33068
2022-07-03 | 68.88% | 50.69% | 7454.7049 | 33064
2022-07-04 | 68.82% | 50.67% | 7458.883 | 33032
2022-07-05 | 68.82% | 50.63% | 7464.0919 | 33032
2022-07-06 | 68.83% | 50.62% | 7465.3394 | 33036
2022-07-07 | 68.97% | 50.62% | 7466.0442 | 33104
2022-07-08 | 68.83% | 50.61% | 7467.7675 | 33036
2022-07-09 | 68.99% | 50.66% | 7459.2314 | 33116
2022-07-10 | 69.33% | 50.74% | 7448.3546 | 33280
2022-07-11 | 68.61% | 50.77% | 7443.7831 | 32932
2022-07-12 | 68.73% | 50.79% | 7440.4738 | 32992
2022-07-13 | 68.69% | 50.77% | 7443.8946 | 32972
2022-07-14 | 68.57% | 50.74% | 7448.0394 | 32912
2022-07-15 | 68.5% | 50.72% | 7450.9241 | 32880
2022-07-16 | 68.38% | 50.7% | 7454.1852 | 32824
2022-07-17 | 67.34% | 50.67% | 7457.6588 | 32324
2022-07-18 | 66.78% | 50.57% | 7472.8535 | 32056
2022-07-19 | 67.03% | 50.55% | 7476.011 | 32172
2022-07-20 | 65.17% | 50.49% | 7485.5505 | 31280
2022-07-21 | 66.69% | 50.54% | 7477.4488 | 32012
2022-07-22 | 65.14% | 50.36% | 7503.5355 | 31268
2022-07-23 | 64.08% | 50.23% | 7523.8191 | 30760
2022-07-24 | 66.14% | 50.42% | 7494.6632 | 31748
2022-07-25 | 66.09% | 50.43% | 7494.3397 | 31724
2022-07-26 | 66.24% | 50.36% | 7503.7996 | 31796
2022-07-27 | 63.23% | 50.02% | 7555.7662 | 30352
2022-07-28 | 64.09% | 50.11% | 7542.3511 | 30764
2022-07-29 | 64.07% | 50.03% | 7553.0522 | 30752
2022-07-30 | 63.81% | 50.13% | 7539.2069 | 30628
2022-07-31 | 65.68% | 50.34% | 7507.1209 | 31528
2022-08-01 | 65.64% | 50.57% | 7473.5443 | 31508
2022-08-02 | 65.56% | 50.66% | 7459.3985 | 31468
2022-08-03 | 64.82% | 50.74% | 7448.1674 | 31112
2022-08-04 | 63.8% | 50.16% | 7533.6575 | 30624
2022-08-05 | 66.66% | 50.37% | 7503.4234 | 31996
2022-08-06 | 72.31% | 51.22% | 7378.45 | 34708
2022-08-07 | 72.25% | 51.19% | 7383.0168 | 34680
2022-08-08 | 72.16% | 51.15% | 7388.1583 | 34636
2022-08-09 | 72.09% | 51.13% | 7391.7603 | 34604
2022-08-10 | 72.02% | 51.09% | 7396.7173 | 34572
2022-08-11 | 68.98% | 51.04% | 7404.6926 | 33112
2022-08-12 | 67.8% | 51.17% | 7385.1031 | 32544
2022-08-13 | 67.73% | 51.23% | 7376.1575 | 32508
2022-08-14 | 67.66% | 51.21% | 7379.5972 | 32476
2022-08-15 | 67.49% | 50.76% | 7445.4956 | 32396
2022-08-16 | 69.79% | 51% | 7409.6193 | 33500
2022-08-17 | 77.27% | 52.07% | 7257.1978 | 37088
2022-08-18 | 77.26% | 52.08% | 7255.6919 | 37084
2022-08-19 | 77.22% | 52.07% | 7257.913 | 37068
2022-08-20 | 77.2% | 52% | 7267.8849 | 37056
2022-08-21 | 77.25% | 51.96% | 7273.7578 | 37080
2022-08-22 | 77.24% | 51.97% | 7271.364 | 37076
2022-08-23 | 77.15% | 51.93% | 7276.7657 | 37032
2022-08-24 | 77.06% | 51.91% | 7279.8627 | 36988
2022-08-25 | 77.04% | 51.91% | 7279.9428 | 36980
2022-08-26 | 76.94% | 51.91% | 7279.4706 | 36932
2022-08-27 | 76.88% | 51.88% | 7284.0419 | 36904
2022-08-28 | 76.83% | 51.86% | 7287.1029 | 36880
2022-08-29 | 76.81% | 51.86% | 7287.3221 | 36868
2022-08-30 | 76.79% | 51.85% | 7288.4432 | 36860
2022-08-31 | 76.76% | 51.85% | 7289.0544 | 36844
2022-09-01 | 76.62% | 51.79% | 7296.309 | 36780
2022-09-02 | 76.27% | 51.81% | 7293.7976 | 36608
2022-09-03 | 75.28% | 51.8% | 7295.028 | 36136
2022-09-04 | 76.28% | 51.81% | 7294.0256 | 36616
2022-09-05 | 76.08% | 51.83% | 7291.8235 | 36520
2022-09-06 | 75.85% | 51.77% | 7299.6772 | 36408
2022-09-07 | 75.64% | 51.76% | 7300.6356 | 36308
2022-09-08 | 75.62% | 51.71% | 7307.6453 | 36296
2022-09-09 | 75.39% | 51.7% | 7309.3892 | 36188
2022-09-10 | 74.97% | 51.67% | 7313.2743 | 35984
2022-09-11 | 75.47% | 51.72% | 7306.3763 | 36224
2022-09-12 | 75.04% | 51.67% | 7313.7681 | 36020
2022-09-13 | 74.47% | 51.64% | 7318.5518 | 35744
2022-09-14 | 75.28% | 51.63% | 7319.8735 | 36136
2022-09-15 | 75.28% | 51.66% | 7315.4595 | 36136
2022-09-16 | 75.29% | 51.68% | 7312.1772 | 36140
2022-09-17 | 75.21% | 51.65% | 7317.1879 | 36100
2022-09-18 | 75.05% | 51.57% | 7327.4007 | 36024
2022-09-19 | 75.02% | 51.58% | 7325.9752 | 36012
2022-09-20 | 74.68% | 51.57% | 7327.7012 | 35848
2022-09-21 | 72.98% | 51.48% | 7340.6263 | 35032
2022-09-22 | 73.08% | 51.56% | 7330.148 | 35080
2022-09-23 | 72.94% | 51.61% | 7323.1059 | 35012
2022-09-24 | 73.3% | 51.82% | 7293.322 | 35184
2022-09-25 | 73.47% | 51.84% | 7289.8408 | 35264
2022-09-26 | 73.47% | 51.8% | 7295.1725 | 35264
2022-09-27 | 73.43% | 51.79% | 7296.9753 | 35248
2022-09-28 | 73.36% | 51.78% | 7298.5232 | 35212
2022-09-29 | 74.49% | 51.84% | 7290.3317 | 35756
2022-09-30 | 74.44% | 51.78% | 7298.3756 | 35732
2022-10-01 | 74.33% | 51.77% | 7299.1727 | 35680
2022-10-02 | 74.29% | 51.77% | 7299.6472 | 35660
2022-10-03 | 74.37% | 51.78% | 7298.2842 | 35696
2022-10-04 | 74.21% | 51.74% | 7303.8101 | 35620
2022-10-05 | 74.12% | 51.73% | 7306.0013 | 35580
2022-10-06 | 74.09% | 51.71% | 7308.036 | 35564
2022-10-07 | 74.03% | 51.71% | 7308.7042 | 35536
2022-10-08 | 73.42% | 51.68% | 7312.0631 | 35244
2022-10-09 | 73.78% | 51.64% | 7317.5039 | 35416
2022-10-10 | 73.68% | 51.62% | 7320.9317 | 35368
2022-10-11 | 73.74% | 51.62% | 7320.5726 | 35396
2022-10-12 | 73.75% | 51.66% | 7314.926 | 35400
2022-10-13 | 73.74% | 51.65% | 7316.3453 | 35396
2022-10-14 | 73.64% | 51.62% | 7321.0705 | 35348
2022-10-15 | 73.62% | 51.61% | 7322.417 | 35336
2022-10-16 | 73.66% | 51.63% | 7319.6464 | 35356
2022-10-17 | 73.56% | 51.62% | 7320.4627 | 35308
2022-10-18 | 73.53% | 51.61% | 7322.1235 | 35296
2022-10-19 | 73.48% | 51.61% | 7322.1356 | 35272
2022-10-20 | 73.23% | 51.61% | 7321.9742 | 35152
2022-10-21 | 73.14% | 51.61% | 7322.7553 | 35108
2022-10-22 | 73.12% | 51.59% | 7325.0093 | 35096
2022-10-23 | 73.11% | 51.6% | 7323.6112 | 35092
2022-10-24 | 73.12% | 51.6% | 7323.2951 | 35096
2022-10-25 | 73.04% | 51.57% | 7328.5353 | 35060
2022-10-26 | 73% | 51.57% | 7328.1239 | 35040
2022-10-27 | 72.98% | 51.58% | 7326.5957 | 35032
2022-10-28 | 73.01% | 51.6% | 7324.1083 | 35044
2022-10-29 | 72.97% | 51.58% | 7326.2367 | 35028
2022-10-30 | 72.92% | 51.55% | 7330.245 | 35004
2022-10-31 | 72.85% | 51.53% | 7334.259 | 34968
2022-11-01 | 72.79% | 51.51% | 7336.1337 | 34940
2022-11-02 | 72.83% | 51.53% | 7334.3564 | 34960
2022-11-03 | 72.82% | 51.52% | 7334.6351 | 34956
2022-11-04 | 72.9% | 51.53% | 7333.403 | 34992
2022-11-05 | 72.96% | 51.47% | 7342.1986 | 35020
2022-11-06 | 72.96% | 51.45% | 7345.0504 | 36480
2022-11-07 | 72.85% | 51.43% | 7348.4998 | 34968
2022-11-08 | 72.67% | 51.37% | 7356.5598 | 34884
2022-11-09 | 72.63% | 51.43% | 7348.3274 | 34864
2022-11-10 | 72.73% | 51.43% | 7348.0217 | 34912
2022-11-11 | 72.72% | 51.46% | 7344.1719 | 34904
2022-11-12 | 72.72% | 51.47% | 7341.9321 | 34908
2022-11-13 | 72.73% | 51.47% | 7342.8678 | 34912
2022-11-14 | 72.69% | 51.46% | 7343.7848 | 34892
2022-11-15 | 72.04% | 51.43% | 7347.5965 | 34580
2022-11-16 | 72.08% | 51.47% | 7342.6253 | 34596
2022-11-17 | 72.28% | 51.5% | 7338.637 | 34692
2022-11-18 | 72.22% | 51.48% | 7340.7772 | 34664
2022-11-19 | 72.25% | 51.5% | 7337.9061 | 34680
2022-11-20 | 71.47% | 51.53% | 7333.0834 | 34304
2022-11-21 | 70.89% | 51.46% | 7343.2311 | 34028
2022-11-22 | 72.07% | 51.47% | 7341.9598 | 34592
2022-11-23 | 72.12% | 51.46% | 7343.2761 | 34620
2022-11-24 | 70.28% | 51.43% | 7348.5578 | 33736
2022-11-25 | 72.02% | 51.41% | 7350.3483 | 34568
2022-11-26 | 71.85% | 51.35% | 7359.6704 | 34488
2022-11-27 | 71.7% | 51.32% | 7364.3477 | 34416
2022-11-28 | 71.71% | 51.24% | 7375.0485 | 34420
2022-11-29 | 71.68% | 51.22% | 7377.5037 | 34408
2022-11-30 | 71.47% | 51.23% | 7376.8119 | 34304
2022-12-01 | 71.36% | 51.2% | 7380.704 | 34252
2022-12-02 | 70.17% | 51.19% | 7382.495 | 33680
2022-12-03 | 70.36% | 51.09% | 7397.5371 | 33772
2022-12-04 | 71.49% | 51.23% | 7377.4014 | 34316
2022-12-05 | 71.44% | 51.22% | 7377.7624 | 34292
2022-12-06 | 71.43% | 51.22% | 7377.6858 | 34284
2022-12-07 | 71.43% | 51.23% | 7376.5758 | 34284
2022-12-08 | 71.44% | 51.23% | 7376.8171 | 34292
2022-12-09 | 71.43% | 51.21% | 7379.502 | 34284
2022-12-10 | 70.36% | 51.32% | 7363.9156 | 33772
2022-12-11 | 70.27% | 51.32% | 7364.1727 | 33728
2022-12-12 | 70.19% | 51.32% | 7363.4036 | 33692
2022-12-13 | 69.02% | 51.23% | 7376.2263 | 33128
2022-12-14 | 70.04% | 51.36% | 7358.15 | 33620
2022-12-15 | 69.88% | 51.37% | 7356.5533 | 33544
2022-12-16 | 69.82% | 51.23% | 7376.1294 | 33512
2022-12-17 | 70.39% | 51.18% | 7384.5758 | 33788
2022-12-18 | 70.3% | 51.11% | 7394.0503 | 33744
2022-12-19 | 68.06% | 51.02% | 7407.266 | 32668
2022-12-20 | 70.08% | 51.11% | 7393.6504 | 33640
2022-12-21 | 70.13% | 51.08% | 7398.9231 | 33664
2022-12-22 | 70.01% | 51.05% | 7402.6196 | 33604
2022-12-23 | 70.01% | 51.07% | 7400.0169 | 33604
2022-12-24 | 70.03% | 51.08% | 7399.0268 | 33612
2022-12-25 | 69.97% | 51.09% | 7397.4756 | 33584
2022-12-26 | 68.82% | 51.01% | 7408.6082 | 33032
2022-12-27 | 69.75% | 51.02% | 7406.9995 | 33480
2022-12-28 | 69.62% | 51.06% | 7401.5744 | 33416
2022-12-29 | 69.54% | 51.07% | 7399.451 | 33380
2022-12-30 | 68.97% | 51.04% | 7404.4348 | 33104
2022-12-31 | 68.03% | 51.01% | 7408.5288 | 32652
2023-01-01 | 68.49% | 51.13% | 7390.5348 | 32876
2023-01-02 | 68.84% | 51.15% | 7388.5867 | 33044
2023-01-03 | 68.75% | 51.14% | 7390.2261 | 33000
2023-01-04 | 68.67% | 51.08% | 7398.6887 | 32960
2023-01-05 | 68.67% | 51.07% | 7399.7135 | 32960
2023-01-06 | 68.67% | 51.09% | 7396.7234 | 32960
2023-01-07 | 68.57% | 51.03% | 7405.1307 | 32912
2023-01-08 | 68.47% | 50.99% | 7411.4618 | 32868
2023-01-09 | 68.27% | 50.95% | 7417.4138 | 32772
2023-01-10 | 67.92% | 50.96% | 7416.0033 | 32600
2023-01-11 | 67.88% | 50.95% | 7416.9361 | 32580
2023-01-12 | 67.85% | 50.95% | 7417.0703 | 32568
2023-01-13 | 67.78% | 50.91% | 7423.1196 | 32536
2023-01-14 | 67.53% | 50.78% | 7441.7802 | 32416
2023-01-15 | 67.46% | 50.83% | 7434.6255 | 32380
2023-01-16 | 65.71% | 50.93% | 7420.3486 | 31540
2023-01-17 | 65.69% | 50.8% | 7438.7174 | 31532
2023-01-18 | 67.56% | 50.93% | 7419.6531 | 32428
2023-01-19 | 67.74% | 50.96% | 7415.2374 | 32516
2023-01-20 | 67.82% | 51% | 7410.0992 | 32552
2023-01-21 | 67.84% | 51.01% | 7408.8522 | 32564
2023-01-22 | 67.84% | 51% | 7410.3197 | 32564
2023-01-23 | 66.59% | 51% | 7410.1262 | 31964
2023-01-24 | 65.86% | 50.89% | 7426.2938 | 31612
2023-01-25 | 67.38% | 50.97% | 7414.1597 | 32340
2023-01-26 | 66.51% | 50.82% | 7436.4069 | 31924
2023-01-27 | 67.61% | 50.96% | 7416.147 | 32452
2023-01-28 | 66.69% | 50.91% | 7423.4512 | 32012
2023-01-29 | 66.52% | 50.75% | 7446.8486 | 31928
2023-01-30 | 67.24% | 50.79% | 7440.1654 | 32276
2023-01-31 | 67.27% | 50.76% | 7445.6428 | 32288
2023-02-01 | 66.47% | 50.89% | 7426.2316 | 31908
2023-02-02 | 66.96% | 50.93% | 7420.3612 | 32140
2023-02-03 | 66.94% | 50.9% | 7424.0917 | 32132
2023-02-04 | 66.53% | 50.86% | 7431.0823 | 31932
2023-02-05 | 65.87% | 50.9% | 7424.4677 | 31616
2023-02-06 | 65.81% | 50.88% | 7426.8841 | 31588
2023-02-07 | 63.69% | 50.77% | 7443.447 | 30572
2023-02-08 | 62.37% | 50.73% | 7449.5719 | 29936
2023-02-09 | 61.26% | 50.64% | 7463.2897 | 29404
2023-02-10 | 64.25% | 51.03% | 7406.3063 | 30840
2023-02-11 | 64.95% | 51.07% | 7400.464 | 31176
2023-02-12 | 64.88% | 51.01% | 7408.1284 | 31144
2023-02-13 | 64.79% | 50.97% | 7413.9914 | 31100
2023-02-14 | 64.79% | 50.95% | 7416.8705 | 31100
2023-02-15 | 64.78% | 50.95% | 7417.3565 | 31096
2023-02-16 | 64.58% | 50.91% | 7423.0181 | 31000
2023-02-17 | 64.53% | 50.9% | 7425.0543 | 30972
2023-02-18 | 64.42% | 50.67% | 7457.7156 | 30920
2023-02-19 | 65.53% | 50.56% | 7474.8336 | 31452
2023-02-20 | 66.07% | 50.61% | 7466.4986 | 31712
2023-02-21 | 65.88% | 50.53% | 7479.0734 | 31624
2023-02-22 | 65.81% | 50.46% | 7488.7344 | 31588
2023-02-23 | 65.88% | 50.5% | 7482.9499 | 31624
2023-02-24 | 65.73% | 50.44% | 7492.7512 | 31552
2023-02-25 | 65.8% | 50.49% | 7485.2818 | 31584
2023-02-26 | 65.76% | 50.51% | 7482.5404 | 31564
2023-02-27 | 65.58% | 50.5% | 7483.647 | 31476
2023-02-28 | 65.54% | 50.5% | 7484.083 | 31460
2023-03-01 | 65.51% | 50.48% | 7486.3589 | 31444
2023-03-02 | 65.75% | 50.51% | 7482.2428 | 31560
2023-03-03 | 65.78% | 50.5% | 7482.8401 | 31576
2023-03-04 | 65.71% | 50.47% | 7488.5331 | 31540
2023-03-05 | 65.7% | 50.49% | 7484.4981 | 31536
2023-03-06 | 64.68% | 50.58% | 7472.1166 | 31044
2023-03-07 | 64.59% | 50.59% | 7470.5574 | 31004
2023-03-08 | 64.46% | 50.6% | 7469.108 | 30940
2023-03-09 | 64.39% | 50.56% | 7475.124 | 30908
2023-03-10 | 64.48% | 50.6% | 7468.0018 | 30952
2023-03-11 | 64.51% | 50.6% | 7468.5364 | 30964
2023-03-12 | 64.71% | 50.5% | 7483.2087 | 29768
2023-03-13 | 65.62% | 50.62% | 7465.8464 | 31500
2023-03-14 | 65.49% | 50.53% | 7478.6088 | 31436
2023-03-15 | 65.46% | 50.53% | 7478.2198 | 31420
2023-03-16 | 65.41% | 50.5% | 7483.0426 | 31396
2023-03-17 | 65.36% | 50.48% | 7486.888 | 31372
2023-03-18 | 65.28% | 50.46% | 7488.8923 | 31332
2023-03-19 | 65.21% | 50.46% | 7489.5092 | 31300
2023-03-20 | 65.32% | 50.52% | 7480.4485 | 31352
2023-03-21 | 65.04% | 50.37% | 7503.1596 | 31220
2023-03-22 | 65.05% | 50.41% | 7496.6662 | 31224
2023-03-23 | 65.19% | 50.5% | 7483.2058 | 31292
2023-03-24 | 65.25% | 50.53% | 7479.5983 | 31320
2023-03-25 | 65.24% | 50.53% | 7479.4872 | 31316
2023-03-26 | 65.28% | 50.55% | 7475.4061 | 31336
2023-03-27 | 65.32% | 50.57% | 7473.4537 | 31352
2023-03-28 | 65.27% | 50.54% | 7476.8908 | 31328
2023-03-29 | 65.07% | 50.54% | 7477.815 | 31232
2023-03-30 | 64.88% | 50.54% | 7477.8745 | 31144
2023-03-31 | 64.98% | 50.57% | 7473.4642 | 31192
2023-04-01 | 64.96% | 50.54% | 7477.8937 | 31180
2023-04-02 | 64.92% | 50.52% | 7480.3031 | 31160
2023-04-03 | 64.88% | 50.49% | 7484.7533 | 31140
2023-04-04 | 64.88% | 50.49% | 7485.5757 | 31144
2023-04-05 | 64.94% | 50.46% | 7489.3976 | 31172
2023-04-06 | 64.86% | 50.44% | 7492.8672 | 31132
2023-04-07 | 64.71% | 50.41% | 7496.4558 | 31060
2023-04-08 | 64.71% | 50.54% | 7478.0908 | 31060
2023-04-09 | 64.72% | 50.53% | 7478.7603 | 31068
2023-04-10 | 64.64% | 50.51% | 7481.2376 | 31028
2023-04-11 | 64.58% | 50.58% | 7472.221 | 30996
2023-04-12 | 64.51% | 50.55% | 7476.2301 | 30964
2023-04-13 | 64.47% | 50.52% | 7479.942 | 30944
2023-04-14 | 64.46% | 50.52% | 7479.7639 | 30940
2023-04-15 | 64.5% | 50.56% | 7474.883 | 30960
2023-04-16 | 64.37% | 50.57% | 7473.3389 | 30896
2023-04-17 | 64.28% | 50.54% | 7477.3413 | 30852
2023-04-18 | 61.21% | 50.67% | 7458.6006 | 29380
2023-04-19 | 58.17% | 50.52% | 7479.9222 | 27924
2023-04-20 | 62.28% | 51.38% | 7355.1378 | 29892
2023-04-21 | 72.24% | 52.44% | 7206.7992 | 34676
2023-04-22 | 83.12% | 53.54% | 7058.0062 | 39896
2023-04-23 | 83.99% | 53.85% | 7017.2207 | 40316
2023-04-24 | 83.97% | 53.86% | 7016.9308 | 40304
2023-04-25 | 84.03% | 53.76% | 7030.1037 | 40336
2023-04-26 | 84.32% | 53.75% | 7031.4269 | 40472
2023-04-27 | 84.68% | 53.7% | 7037.5588 | 40648
2023-04-28 | 86.43% | 53.83% | 7019.8667 | 41488
2023-04-29 | 86.34% | 53.87% | 7014.5817 | 41444
2023-04-30 | 86.33% | 53.86% | 7017.0028 | 41440
2023-05-01 | 85.77% | 53.83% | 7021.0826 | 41168
2023-05-02 | 85.72% | 53.83% | 7020.0788 | 41148
2023-05-03 | 85.48% | 53.77% | 7028.5371 | 41032
2023-05-04 | 85.56% | 53.81% | 7023.5226 | 41068
2023-05-05 | 85.58% | 53.79% | 7025.6146 | 41080
2023-05-06 | 85.85% | 53.73% | 7034.0539 | 41208
2023-05-07 | 87.64% | 53.8% | 7024.738 | 42068
2023-05-08 | 87.75% | 53.9% | 7011.7966 | 42120
2023-05-09 | 87.45% | 54.03% | 6994.601 | 41976
2023-05-10 | 87.22% | 54.04% | 6992.8891 | 41868
2023-05-11 | 87.56% | 54.09% | 6986.8459 | 42028
2023-05-12 | 87.6% | 54.15% | 6978.9678 | 42048
2023-05-13 | 87.11% | 53.93% | 7007.5485 | 41812
2023-05-14 | 87.22% | 53.96% | 7003.3354 | 41864
2023-05-15 | 89.68% | 54.15% | 6979.005 | 43044
2023-05-16 | 89.92% | 54.1% | 6985.9148 | 43164
2023-05-17 | 89.9% | 54.05% | 6991.6156 | 43152
2023-05-18 | 89.93% | 54.06% | 6990.4191 | 43168
2023-05-19 | 89.95% | 54.07% | 6988.7766 | 43176
2023-05-20 | 89.96% | 54.07% | 6988.8178 | 43180
2023-05-21 | 89.88% | 54.03% | 6993.9692 | 43144
2023-05-22 | 89.84% | 54.02% | 6995.3426 | 43124
2023-05-23 | 89.84% | 54.02% | 6995.1675 | 43124
2023-05-24 | 89.73% | 54.03% | 6995.0115 | 43072
2023-05-25 | 123.7% | 74.61% | 5064.8196 | 42552
2023-05-26 | 89.77% | 54.03% | 6994.0961 | 43088
2023-05-27 | 89.93% | 54.03% | 6994.9343 | 43168
2023-05-28 | 89.92% | 54.03% | 6994.6526 | 43160
2023-05-29 | 89.87% | 54.01% | 6997.3409 | 43136
2023-05-30 | 89.87% | 54.02% | 6996.2306 | 43136
2023-05-31 | 89.95% | 54.07% | 6989.4232 | 43176
2023-06-01 | 89.92% | 54.1% | 6984.8445 | 43160

## Definition
Description of Data Fields
Total Output Factor (%) | Total system output calculated by dividing actual power output over a given period of time by the potential power output while operating at name plate capacity
AC Efficiency (%, LHV) | Energy output per energy input calculated as LHV efficiency based on LHV to HHV, kWh to BTU, and Therms to BTU conversion ratios
Heat Rate (BTU/kWh, HHV) | Heat rate is calculated as BTU/kWh
Electricity Out (kWh) | Amount of electricity produced; measured at the transformer and after the inverter, in the electrical connection (480V @ 60Hz, 4-wire 3 phase)
AC Efficiency Calculation Formula (LHV)